## point_list
Mount Vernon P231951 W8 | Name | Type | Object ID | Device ID | Object Name | Read/Write | Unit | Min. | Max. | Normal Status | Description
PPH200-MAIN PROGRAM-1 | General Alarm Status | BBV | BV:7 | DEV:10001 | general_alarm_status_1 | R | - | 0 : Alarm is not active | 1 : Alarm is active | 0 : Alarm is not active | General alarm status
| fire alarm | BALM | BV:42 | DEV:10001 | fire_alarm_1 | R | - | 0 : Alarm is not active | 1 : Alarm is active | 0 : Alarm is not active | Fire alarm
| comp1_liq_pr | BAV | AV:100 | DEV:10001 | comp1_liq_pr_2 | R | PSI | 0 | 667 | - | Cir.1 Liquid Pressure Reading
| comp1_suc_pr | BAV | AV:101 | DEV:10001 | comp1_suc_pr_2 | R | PSI | 0 | 250 | - | Cir.1 Suction Pressure Reading
| comp2_liq_pr | BAV | AV:102 | DEV:10001 | comp2_liq_pr_2 | R | PSI | 0 | 667 | - | Cir.2 Liquid Pressure Reading
| comp2_SUC_pr | BAV | AV:103 | DEV:10001 | comp2_suc_pr_2 | R | PSI | 0 | 250 | - | Cir.2 Suction Pressure Reading
| comp3_liq_pr | BAV | AV:104 | DEV:10001 | comp3_liq_pr_2 | R | PSI | 0 | 667 | - | Cir.3Liquid Pressure Reading
| comp4_liq_pr | BAV | AV:106 | DEV:10001 | comp4_liq_pr_2 | R | PSI | 0 | 667 | - | Cir.4 Liquid Pressure Reading
| comp4_SUC_pr | BAV | AV:107 | DEV:10001 | comp4_suc_pr_2 | R | PSI | 0 | 250 | - | Cir.4 Suction Pressure Reading
| DA1 TEMP | BAV | AV:108 | DEV:10001 | da1_temp_2 | R | °F | -45 | 290 | - | Discharge Temp. CIRCUIT.#1
| DA2 TEMP | BAV | AV:109 | DEV:10001 | da2_temp_2 | R | °F | -45 | 290 | - | Discharge Temp. CIRCUIT.#2
| DA3 TEMP | BAV | AV:140 | DEV:10001 | da3_temp_2 | R | °F | -45 | 290 | - | Discharge Temp. CIRCUIT.#3
| DA4 TEMP | BAV | AV:141 | DEV:10001 | da4_temp_2 | R | °F | -45 | 290 | - | Discharge Temp. CIRCUIT.#4
| DX AIR TEMP1 | BAV | AV:110 | DEV:10001 | dx_air_temp1_2 | R | °F | -45 | 190 | - | Dx. Leaving Air temperature#1 Reading
| DX AIR TEMP2 | BAV | AV:111 | DEV:10001 | dx_air_temp2_2 | R | °F | -45 | 190 | - | Dx. Leaving Air temperature#2 Reading
| OAT SENSOR | BAV | AV:119 | DEV:10001 | oat_sensor_2 | R | °F | -45 | 190 | - | Outside air temperature Reading
| SAT SENSOR | BAV | AV:126 | DEV:10001 | sat_sensor_2 | R | °F | -45 | 190 | - | Supply air temperature Reading
| SF1 VFD % | BAV | AV:511 | DEV:10001 | sf1_vfd_percent_3 | R | % | 0 | 100 | - | Supply Fan 1VFD Speed %
| SF2 VFD % | BAV | AV:512 | DEV:10001 | sf2_vfd_percent_3 | R | % | 0 | 100 | - | Supply Fan 2VFD Speed %
| SF3 VFD % | BAV | AV:539 | DEV:10001 | sf3_vfd_percent_3 | R | % | 0 | 100 | - | Supply Fan 3VFD Speed %
| SF1-STATUS | BBV | BV:527 | DEV:10001 | sf1-status_3 | R | - | 0 : Supply fan 1motor is Off | 1 : Supply fan1 motor is On | 1 : Supply fan 1motor is On | Supply Fan1 Motor Status
| SF2-STATUS | BBV | BV:528 | DEV:10001 | sf2-status_3 | R | - | 0 : Supply fan 2motor is Off | 1 : Supply fan2 motor is On | 1 : Supply fan2 motor is On | Supply Fan 2Motor Status
| SF3-STATUS | BBV | BV:529 | DEV:10001 | sf3-status_3 | R | - | 0 : Supply fan 3motor is Off | 1 : Supply fan3 motor is On | 1 : Supply fan 3motor is On | Supply Fan3 Motor Status
| SUP_FAN1 Alarm Status | BBV | BV:512 | DEV:10001 | sup_fan1_alarm_status_3 | R | - | 0 : Supply fan 1motor Alarm is not Active | 1 : Supply fan1 motor Alarm is Active | 0 : Supply fan 1motor Alarm is not Active | Supply Fan 1 Motor Alarm
| SUP_FAN2 Alarm Status | BBV | BV:513 | DEV:10001 | sup_fan2_alarm_status_3 | R | - | 0 : Supply fan 1motor Alarm is not Active | 1 : Supply fan1 motor Alarm is Active | 0 : Supply fan 1motor Alarm is not Active | Supply Fan 2 Motor Alarm
| SUP_FAN3 Alarm Status | BBV | BV:531 | DEV:10001 | sup_fan3_alarm_status_3 | R | - | 0 : Supply fan 3motor Alarm is not Active | 1 : Supply fan3 motor Alarm is Active | 0 : Supply fan 3motor Alarm is not Active | Supply Fan 3 Motor Alarm
| C1_HI | BALM | BV:952 | DEV:10001 | c1_hi_4 | R | - | 0 : Circuit#1 High Pressure Switch Alarm is not Active | 1 : Circuit#1 High Pressure Switch Alarm is Active | 0 : Circuit#1 High Pressure Switch Alarm is not Active | Cir.1 High Pressure Switch Alarm
| C1_LPS | BALM | BV:950 | DEV:10001 | c1_lps_4 | R | - | 0 : Circuit#1 Low Pressure Switch Alarm is not Active | 1 : Circuit#1 Low Pressure Switch Alarm is Active | 0 : Circuit#1 Low Pressure Switch Alarm is not Active | Cir.1 Low Pressure Switch Alarm
| C1-STATUS | BBV | BV:801 | DEV:10001 | c1-status_4 | R | - | 0 : Comp.1 is Off | 1 : Comp.1 is On | 1 : Comp.1 is On | Compressor #1 Status
| C2_HI | BALM | BV:959 | DEV:10001 | c2_hi_4 | R | - | 0 : Circuit#2 High Pressure Switch Alarm is not Active | 1 : Circuit#2 High Pressure Switch Alarm is Active | 0 : Circuit#2 High Pressure Switch Alarm is not Active | Cir.2 High Pressure Switch Alarm
| C2_LPS | BALM | BV:956 | DEV:10001 | c2_lps_4 | R | - | 0 : Circuit#2 Low Pressure Switch Alarm is not Active | 1 : Circuit#2 Low Pressure Switch Alarm is Active | 0 : Circuit#2 Low Pressure Switch Alarm is not Active | Cir.2 Low Pressure Switch Alarm
| C2-STATUS | BBV | BV:802 | DEV:10001 | c2-status_4 | R | - | 0 : Comp.2 is Off | 1 : Comp.2 is On | 1 : Comp.2 is On | Compressor #2 Status
| C1_MP | BALM | BV:954 | DEV:10001 | c1_mp_4 | R | - | 0 : Comp.1 Motor protector Alarm is not Active | 1 : Comp.1 Motor protector Alarm is Active | 0 : Comp.1 Motor protector Alarm is not Active | Comp.1 Motor protector Alarm
| C2_MP | BALM | BV:962 | DEV:10001 | c2_mp_4 | R | - | 0 : Comp.2 Motor protector Alarm is not Active | 1 : Comp.2 Motor protector Alarm is Active | 0 : Comp.2 Motor protector Alarm is not Active | Comp.2 Motor protector Alarm
| C3_HI | BALM | BV:966 | DEV:10001 | c3_hi_4 | R | - | 0 : Circuit#3 High Pressure Switch Alarm is not Active | 1 : Circuit#3High Pressure Switch Alarm is Active | 0 : Circuit#3 High Pressure Switch Alarm is not Active | Cir.3 High Pressure Switch Alarm
| C3_LPS | BALM | BV:891 | DEV:10001 | c3_lps_4 | R | - | 0 : Circuit#3 Low Pressure Switch Alarm is not Active | 1 : Circuit#3 Low Pressure Switch Alarm is Active | 0 : Circuit#3 Low Pressure Switch Alarm is not Active | Cir.3Low Pressure Switch Alarm
| C3-STATUS | BBV | BV:803 | DEV:10001 | c3-status_4 | R | - | 0 : Comp.3 is Off | 1 : Comp.3 is On | 1 : Comp.3 is On | Compressor #3 Status
| C4_HI | BALM | BV:896 | DEV:10001 | c4_hi_4 | R | - | 0 : Circuit#4 High Pressure Switch Alarm is not Active | 1 : Circuit#4 High Pressure Switch Alarm is Active | 0 : Circuit#4 High Pressure Switch Alarm is not Active | Cir.4 High Pressure Switch Alarm
| C4_LPS | BALM | BV:897 | DEV:10001 | c4_lps_4 | R | - | 0 : Circuit#4 Low Pressure Switch Alarm is not Active | 1 : Circuit#4 Low Pressure Switch Alarm is Active | 0 : Circuit#4 Low Pressure Switch Alarm is not Active | Cir.4 Low Pressure Switch Alarm
| C4-STATUS | BBV | BV:804 | DEV:10001 | c4-status_4 | R | - | 0 : Comp.4 is Off | 1 : Comp.4 is On | 1 : Comp.4 is On | Compressor #4Status
| C3_MP | BALM | BV:892 | DEV:10001 | c3_mp_4 | R | - | 0 : Comp.3 Motor protector Alarm is not Active | 1 : Comp.3 Motor protector Alarm is Active | 0 : Comp.3 Motor protector Alarm is not Active | Comp.3 Motor protector Alarm
| C4_MP | BALM | BV:898 | DEV:10001 | c4_mp_4 | R | - | 0 : Comp.4 Motor protector Alarm is not Active | 1 : Comp.4 Motor protector Alarm is Active | 0 : Comp.4 Motor protector Alarm is not Active | Comp.4 Motor protector Alarm
| comp1_flt | BBV | BV:826 | DEV:10001 | comp1_flt_4 | R | - | 0 : Compressor#1 Proof Alarm is not Active | 1 : Compressor#1 Proof Alarm is Active | 0 : Compressor#1 Proof Alarm is not Active | Comp.1 Proof Alarm
| comp2_flt | BBV | BV:831 | DEV:10001 | comp2_flt_4 | R | - | 0 : Compressor#2 Proof Alarm is not Active | 1 : Compressor#2 Proof Alarm is Active | 0 : Compressor#2 Proof Alarm is not Active | Comp.2 Proof Alarm
| comp3_flt | BBV | BV:836 | DEV:10001 | comp3_flt_4 | R | - | 0 : Compressor#3 Proof Alarm is not Active | 1 : Compressor#3 Proof Alarm is Active | 0 : Compressor#3 Proof Alarm is not Active | Comp.3 Proof Alarm
| comp4_flt | BBV | BV:841 | DEV:10001 | comp4_flt_4 | R | - | 0 : Compressor#4 Proof Alarm is not Active | 1 : Compressor#4 Proof Alarm is Active | 0 : Compressor#4 Proof Alarm is not Active | Comp.4 Proof Alarm
| Unit Enable (BAS) | BBV | BV:21 | DEV:10001 | enable_bas_1 | R/W | - | 0 : Unit is Off by BMS | 1 : Unit is On by BMS | - | Unit Enable BMS Signal
| Control Source | BMSV | MSV:1 | DEV:10001 | control_source_1 | R/W | - | 1 | 4 | - | Unit Enable source could be set to: 1=for unit enable by hard wire remote switch, 2=for unit enable by the touch keypad, 3=for unit enable by BMS, 4=for unit enable by Schedule
| Cool Setpoint | BAV | AV:844 | DEV:10001 | cool_setpoint_4 | R | °F | 50 | 90 | - | Reading of the cooling setpoint
| COOLING Temp SETPOINT_Write | BAV | AV:846 | DEV:10001 | cooling_temp_setpoint_write_4 | R/W | °F | 50 | 90 | 72 | Adjusting the cooling setpoint
| Enable mode (BMS)_Write | BBV | BV:1001 | DEV:10001 | enable_mode_write_4 | R/W | - | 0: Set the unit in the cooling mode | 1: Set the unit in the heating mode | 0: Set the unit in the cooling mode | Selecting between the heating & cooling mode (this selection is enabled if "Control mode htg/clg" point is set to 1)
| LIQ1 TEMP | BAV | AV:165 | DEV:10001 | liq1_temp_2 | R | °F | -45 | 290 | - | LIQUID Temp. CIRCUIT.#1
| LIQ2 TEMP | BAV | AV:166 | DEV:10001 | liq2_temp_2 | R | °F | -45 | 290 | - | LIQUID Temp. CIRCUIT.#2
| LIQ3 TEMP | BAV | AV:167 | DEV:10001 | liq3_temp_2 | R | °F | -45 | 290 | - | LIQUID Temp. CIRCUIT.#3
| LIQ4 TEMP | BAV | AV:168 | DEV:10001 | liq4_temp_2 | R | °F | -45 | 290 | - | LIQUID Temp. CIRCUIT.#4
| Alarm Reset | BBV | BV:3 | DEV:10001 | alarm_reset_1 | R/W |  |  |  |  | TO RESET ALARM, CHANGE ITS VALUE FROM 0 TO 1 OR 1 TO 0