## point_list
Name | Read/Write | Unit | Min. | Max. | Normal Status | Description
General Alarm Status | R | - | 0 : Alarm is not active | 1 : Alarm is active | 0 : Alarm is not active | General alarm status
fire alarm | R | - | 0 : Alarm is not active | 1 : Alarm is active | 0 : Alarm is not active | Fire alarm
comp1_liq_pr | R | PSI | 0 | 667 | - | Cir.1 Liquid Pressure Reading
comp1_suc_pr | R | PSI | 0 | 250 | - | Cir.1 Suction Pressure Reading
comp2_liq_pr | R | PSI | 0 | 667 | - | Cir.2 Liquid Pressure Reading
comp2_SUC_pr | R | PSI | 0 | 250 | - | Cir.2 Suction Pressure Reading
comp3_liq_pr | R | PSI | 0 | 667 | - | Cir.3Liquid Pressure Reading
comp3_suc_pr | R | PSI | 0 | 250 | - | Cir.3 Suction Pressure Reading
comp4_liq_pr | R | PSI | 0 | 667 | - | Cir.4 Liquid Pressure Reading
comp4_SUC_pr | R | PSI | 0 | 250 | - | Cir.4 Suction Pressure Reading
DA1 TEMP | R | °F | -45 | 290 | - | Discharge Temp. CIRCUIT.#1
DA2 TEMP | R | °F | -45 | 290 | - | Discharge Temp. CIRCUIT.#2
DA3 TEMP | R | °F | -45 | 290 | - | Discharge Temp. CIRCUIT.#3
DA4 TEMP | R | °F | -45 | 290 | - | Discharge Temp. CIRCUIT.#4
DX AIR TEMP1 | R | °F | -45 | 190 | - | Dx. Leaving Air temperature#1 Reading
DX AIR TEMP2 | R | °F | -45 | 190 | - | Dx. Leaving Air temperature#2 Reading
OAT SENSOR | R | °F | -45 | 190 | - | Outside air temperature Reading
SAT SENSOR | R | °F | -45 | 190 | - | Supply air temperature Reading
SF1 VFD % | R | % | 0 | 100 | - | Supply Fan 1VFD Speed %
SF2 VFD % | R | % | 0 | 100 | - | Supply Fan 2VFD Speed %
SF3 VFD % | R | % | 0 | 100 | - | Supply Fan 3VFD Speed %
SF1-STATUS | R | - | 0 : Supply fan 1motor is Off | 1 : Supply fan1 motor is On | 1 : Supply fan 1motor is On | Supply Fan1 Motor Status
SF2-STATUS | R | - | 0 : Supply fan 2motor is Off | 1 : Supply fan2 motor is On | 1 : Supply fan2 motor is On | Supply Fan 2Motor Status
SF3-STATUS | R | - | 0 : Supply fan 3motor is Off | 1 : Supply fan3 motor is On | 1 : Supply fan 3motor is On | Supply Fan3 Motor Status
SUP_FAN1 Alarm Status | R | - | 0 : Supply fan 1motor Alarm is not Active | 1 : Supply fan1 motor Alarm is Active | 0 : Supply fan 1motor Alarm is not Active | Supply Fan 1 Motor Alarm
SUP_FAN2 Alarm Status | R | - | 0 : Supply fan 1motor Alarm is not Active | 1 : Supply fan1 motor Alarm is Active | 0 : Supply fan 1motor Alarm is not Active | Supply Fan 2 Motor Alarm
SUP_FAN3 Alarm Status | R | - | 0 : Supply fan 3motor Alarm is not Active | 1 : Supply fan3 motor Alarm is Active | 0 : Supply fan 3motor Alarm is not Active | Supply Fan 3 Motor Alarm
C1_HPS | R | - | 0 : Circuit#1 High Pressure Switch Alarm is not Active | 1 : Circuit#1 High Pressure Switch Alarm is Active | 0 : Circuit#1 High Pressure Switch Alarm is not Active | Cir.1 High Pressure Switch Alarm
C1_HI | R | - | 0 : Circuit#1 High Pressure Switch Alarm is not Active | 1 : Circuit#1 High Pressure Switch Alarm is Active | 0 : Circuit#1 High Pressure Switch Alarm is not Active | Cir.1 High Pressure Switch Alarm
C1_LPS | R | - | 0 : Circuit#1 Low Pressure Switch Alarm is not Active | 1 : Circuit#1 Low Pressure Switch Alarm is Active | 0 : Circuit#1 Low Pressure Switch Alarm is not Active | Cir.1 Low Pressure Switch Alarm
C1-HPS | R | - | 0 : Circuit#1 High Pressure Switch Alarm is not Active | 1 : Circuit#1 High Pressure Switch Alarm is Active | 0 : Circuit#1 High Pressure Switch Alarm is not Active | Cir.1 High Pressure Switch Alarm
C1-STATUS | R | - | 0 : Comp.1 is Off | 1 : Comp.1 is On | 1 : Comp.1 is On | Compressor #1 Status
C2_HPS | R | - | 0 : Circuit#2 High Pressure Switch Alarm is not Active | 1 : Circuit#2 High Pressure Switch Alarm is Active | 0 : Circuit#2 High Pressure Switch Alarm is not Active | Cir.2 High Pressure Switch Alarm
C2_HI | R | - | 0 : Circuit#2 High Pressure Switch Alarm is not Active | 1 : Circuit#2 High Pressure Switch Alarm is Active | 0 : Circuit#2 High Pressure Switch Alarm is not Active | Cir.2 High Pressure Switch Alarm
C2_LPS | R | - | 0 : Circuit#2 Low Pressure Switch Alarm is not Active | 1 : Circuit#2 Low Pressure Switch Alarm is Active | 0 : Circuit#2 Low Pressure Switch Alarm is not Active | Cir.2 Low Pressure Switch Alarm
C2-STATUS | R | - | 0 : Comp.2 is Off | 1 : Comp.2 is On | 1 : Comp.2 is On | Compressor #2 Status
C1_MP | R | - | 0 : Comp.1 Motor protector Alarm is not Active | 1 : Comp.1 Motor protector Alarm is Active | 0 : Comp.1 Motor protector Alarm is not Active | Comp.1 Motor protector Alarm
C2_MP | R | - | 0 : Comp.2 Motor protector Alarm is not Active | 1 : Comp.2 Motor protector Alarm is Active | 0 : Comp.2 Motor protector Alarm is not Active | Comp.2 Motor protector Alarm
C3_HPS | R | - | 0 : Circuit#3 High Pressure Switch Alarm is not Active | 1 : Circuit#3High Pressure Switch Alarm is Active | 0 : Circuit#3 High Pressure Switch Alarm is not Active | Cir.3 High Pressure Switch Alarm
C3_HI | R | - | 0 : Circuit#3 High Pressure Switch Alarm is not Active | 1 : Circuit#3High Pressure Switch Alarm is Active | 0 : Circuit#3 High Pressure Switch Alarm is not Active | Cir.3 High Pressure Switch Alarm
C3_LPS | R | - | 0 : Circuit#3 Low Pressure Switch Alarm is not Active | 1 : Circuit#3 Low Pressure Switch Alarm is Active | 0 : Circuit#3 Low Pressure Switch Alarm is not Active | Cir.3Low Pressure Switch Alarm
C3-STATUS | R | - | 0 : Comp.3 is Off | 1 : Comp.3 is On | 1 : Comp.3 is On | Compressor #3 Status
C4_HPS | R | - | 0 : Circuit#4 High Pressure Switch Alarm is not Active | 1 : Circuit#4 High Pressure Switch Alarm is Active | 0 : Circuit#4 High Pressure Switch Alarm is not Active | Cir.4 High Pressure Switch Alarm
C4_HI | R | - | 0 : Circuit#4 High Pressure Switch Alarm is not Active | 1 : Circuit#4 High Pressure Switch Alarm is Active | 0 : Circuit#4 High Pressure Switch Alarm is not Active | Cir.4 High Pressure Switch Alarm
C4_LPS | R | - | 0 : Circuit#4 Low Pressure Switch Alarm is not Active | 1 : Circuit#4 Low Pressure Switch Alarm is Active | 0 : Circuit#4 Low Pressure Switch Alarm is not Active | Cir.4 Low Pressure Switch Alarm
C4-STATUS | R | - | 0 : Comp.4 is Off | 1 : Comp.4 is On | 1 : Comp.4 is On | Compressor #4Status
C3_MP | R | - | 0 : Comp.3 Motor protector Alarm is not Active | 1 : Comp.3 Motor protector Alarm is Active | 0 : Comp.3 Motor protector Alarm is not Active | Comp.3 Motor protector Alarm
C4_MP | R | - | 0 : Comp.4 Motor protector Alarm is not Active | 1 : Comp.4 Motor protector Alarm is Active | 0 : Comp.4 Motor protector Alarm is not Active | Comp.4 Motor protector Alarm
comp1_flt | R | - | 0 : Compressor#1 Proof Alarm is not Active | 1 : Compressor#1 Proof Alarm is Active | 0 : Compressor#1 Proof Alarm is not Active | Comp.1 Proof Alarm
comp2_flt | R | - | 0 : Compressor#2 Proof Alarm is not Active | 1 : Compressor#2 Proof Alarm is Active | 0 : Compressor#2 Proof Alarm is not Active | Comp.2 Proof Alarm
comp3_flt | R | - | 0 : Compressor#3 Proof Alarm is not Active | 1 : Compressor#3 Proof Alarm is Active | 0 : Compressor#3 Proof Alarm is not Active | Comp.3 Proof Alarm
comp4_flt | R | - | 0 : Compressor#4 Proof Alarm is not Active | 1 : Compressor#4 Proof Alarm is Active | 0 : Compressor#4 Proof Alarm is not Active | Comp.4 Proof Alarm
Unit Enable (BAS) | R/W | - | 0 : Unit is Off by BMS | 1 : Unit is On by BMS | - | Unit Enable BMS Signal
Control Source | R/W | - | 1 | 4 | - | Unit Enable source could be set to: 1=for unit enable by hard wire remote switch, 2=for unit enable by the touch keypad, 3=for unit enable by BMS, 4=for unit enable by Schedule
Enable mode (BMS) | R/W | - | 0: Set the unit in the cooling mode | 1: Set the unit in the heating mode | 0: Set the unit in the cooling mode | Selecting between the heating & cooling mode (this selection is enabled if "Control mode htg/clg" point is set to 1)
Cool Setpoint | R | °F | 50 | 90 | - | Reading of the cooling setpoint
COOLING Temp SETPOINT_Write | R/W | °F | 50 | 90 | 72 | Adjusting the cooling setpoint
sat_stpt_ht_WRITE | R/W | °F | 65 | 90 | 72 | Adjustingthe heating setpoint
Enable mode (BMS)_Write | R/W | - | 0: Set the unit in the cooling mode | 1: Set the unit in the heating mode | 0: Set the unit in the cooling mode | Selecting between the heating & cooling mode (this selection is enabled if "Control mode htg/clg" point is set to 1)
LIQ1 TEMP | R | °F | -45 | 290 | - | LIQUID Temp. CIRCUIT.#1
LIQ2 TEMP | R | °F | -45 | 290 | - | LIQUID Temp. CIRCUIT.#2
LIQ3 TEMP | R | °F | -45 | 290 | - | LIQUID Temp. CIRCUIT.#3
LIQ4 TEMP | R | °F | -45 | 290 | - | LIQUID Temp. CIRCUIT.#4
Alarm Reset | R/W |  |  |  |  | TO RESET ALARM, CHANGE ITS VALUE FROM 0 TO 1 OR 1 TO 0